## Deficiency list
No. | Building | Level | Location | Deficiency | Spec section | Trade | Subcontractor | Photo | Priority | Identified by | Date identified | Due | Status | Completed on | Back-checked by | Closed on | Notes
D-0412 | A | 7 | Suite 702, conference room | Drywall nail pops, north wall, 6 locations, visible under raking light | 09 29 00 | Drywall | Northline Interiors | IMG_2041.jpg | Standard | M. Alvarez (super) | 2026-09-14 | 2026-09-25 | Closed | 2026-09-23 | M. Alvarez (super) | 2026-09-24 | Back-checked against original photo; all 6 spotted and painted.
D-0413 | A | 7 | Corridor 7B, stair 2 door | Fire-rated door does not self-close and latch from 90°; closer arm loose | 08 71 00 | Doors and hardware | Keystone Door & Hardware | IMG_2043.jpg | Life safety | M. Alvarez (super) | 2026-09-14 | 2026-09-14 | Closed | 2026-09-14 | R. Chen (QA) | 2026-09-14 | Closer re-fixed same day; latching confirmed three times.
D-0414 | A | 7 | Suite 704, open office, grid C/4 | Supply diffuser not connected; flex duct lying on ceiling tile | 23 37 13 | Mechanical | Summit Mechanical | IMG_2047.jpg | High | J. Patel (architect field rep) | 2026-09-15 | 2026-09-17 | Ready for back-check | 2026-09-17 |  |  | Ceiling tile at C/4 to be replaced by ACT sub after.
D-0415 | A | 7 | Suite 702, kitchenette | Base cabinet door misaligned; 1/8 in proud of adjacent door | 06 41 00 | Millwork | Cedar Ridge Millwork | IMG_2050.jpg | Standard | J. Patel (architect field rep) | 2026-09-15 | 2026-09-26 | Disputed |  |  |  | Sub says hinge damaged by tenant move-in; photo from 15 Sep predates move-in. Re-issued.

## What each column is for
Column | What it is for
No. | Permanent number, never reused, never encodes floor, room or sub.
Building | Building or phase.
Level | Floor or level.
Location | Suite, room or gridline, from an agreed list.
Deficiency | What is wrong, where on the thing, and how much of it.
Spec section | The specification section or drawing the work falls short of.
Trade | The scope the work belongs to.
Subcontractor | The company responsible.
Photo | Filename of the photo taken when found.
Priority | Life safety, High or Standard.
Identified by | Who found it.
Date identified | Date found, not date entered.
Due | Fix-by date, visible to the sub.
Status | The sub moves a row as far as Ready for back-check; your side closes it.
Completed on | Date the sub said it was done.
Back-checked by | Who checked the fix against the original photo.
Closed on | Date back-checked and closed.
Notes | The dispute, the re-issue, the access arrangement.
From issuesid.com/deficiency-list-template/ - the page explains the columns, four worked deficiencies, and where a deficiency list breaks.